Bare Finish Steel Raised Floor

Abeite Bare Finish Steel Raised Floor is a new patent “cross strengthening rib”

and “concave rib structure”, which can enhance 10-30% more loading capacity. From

the selection of materials, procurement, production, packaging, are following with

the Chinese and PSA MOB PS/SPU、DIN EN 12825 specifications.

Construction:

Bare Steel Raised Floor is manufactured from cold-rolled steel resistance welded, lightweight

cement infilled. This raised floor system is composed of panels, pedestals, anti-vibration

gasket and screws. The panel is placed on top of the pedestals with an anti-vibration gasket

and then locked in place with the screws in the corner-lock holes.

| Type: | FS662-2000 |
| --- | --- |
| Finished Floor Height: | 50-1000mm |
| Panel Size: | 500*500*28mm、600*600*33mm、610*610mm |
| Edge Trim Type: | Bent edge/Cut edge |
| Trunking | Available |
| Grommet Hole | Available |
| Installation: | Without or With Stringer System |

Intelligent Network Raised Floor                  Low Profile Raised Floor

Cutout Bare Panel                    Bolted Stringer System

Characteristics:

- Epoxy paint for lifetime protection;

- Tolerance of panel size is 0-0.40mm; Tolerance of panel thickness is ±0.30mm;

Un-flatness is ≤0.60mm;

- The load performance is strong;

- Class A flame spread & smoke-developed index

- OEM is available;

Applications:

Office building, intelligent office environment, meeting room, commercial and industrial bureau,

government, places that have requirements of dust-proof and water-proof, fields with requirements,

usually used with square carpet.

Specification:

| Type | Size | Concertrated Load Defleation≤2.5mm |  |  | Uniform Load | Ultimate Load | System Resistance |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | mm | LBS | KN | KG | KN/㎡ | KN | Ω |
| FS662 | 600*600 (500*500/ 610*610 is optional) | 662 | 2.95 | 300 | 12.50 | 8.85 | 1.0x106-1.0x109 |
| FS800 |  | 800 | 3.56 | 363 | 16.10 | 10.68 |  |
| FS1000 |  | 1000 | 4.45 | 454 | 23.00 | 13.35 |  |
| FS1250 |  | 1250 | 5.56 | 567 | 33.00 | 16.68 |  |
| FS1500 |  | 1500 | 6.67 | 680 | 34.50 | 20.02 |  |
| FS2000 |  | 2000 | 8.90 | 906 | 46.00 | 26.70 |  |

Understructures:

| Product name: | Pedestal |
| --- | --- |
| Type: | Flat Head |
| Height: | FFH50-600mm |
| Top plate: | 75*75*3.0mm |
| Base plate:: | 95*95*2.0mm |
| Threaded rod: | M18/20 |
| Surface: | Cold galvanizing Hot galvanizing Powder coated |
| Gasket: | Without |

| Product name: | Pedestal |
| --- | --- |
| Type: | Cross Head (Aluminum and steel is optional) |
| Height: | FFH50-600mm |
| Top plate: | 70*70mm |
| Base plate:: | 95*95*3.0mm |
| Threaded rod: | M18/20 |
| Surface: | Cold galvanizing Hot galvanizing Powder coated |
| Gasket: | With |

Changzhou Abeite Computer Room Equipment Co.,Ltd

Add: No. 108, Chaoyang Village, Hengshanqiao Town, Wujin District,

Changzhou City, Jiangsu Province，China

Tel: +86(519)86056270

Fax: +86(519)86056270

E-mail: info@abeiteraisedfloor.com

Web: www.abeiteraisedfloor.com